## Modbus Settings
Modbus protocol settings
Mode: | RTU | Default
Baudrate | 209. ModbusBaudrate (0=9600 , 1 = 19200) | 1 | 19200
Start bits | 1 | 1 | 1
Data bits | 8 | 8 | 8
Stop Bits | 1 stop bit at Even or Odd, 2 stop bit at None | 1 | 1
Parity | 210. ModbusParität (0=Keine, 1=Gerade, 2=Ungerade) | 1 | Gerade
Address | 208. ModbusAdresse (1-247) | 20 | 20
Registers Map
Support function | 3 - Read Holding Registers 4 - Read Input Registers 6 - Write Single Registers 17 - Internal use for Datalogger
This parameters can be changed:
Baudrate (209), Parity (210.), Modbus address (208.)
All Setpoints and Datapoints are unsigned integers 16-bit

## Setpoints
Modbus Setpoints ES1015 |  | Funktionscode Lesen: 03 | Holding register (4x) Read/Write
Funktionscode Schreiben: 06
Name | Description | Beschreibung | Address | Min | Max | Decimal | Offset | Ab Firmware Version
Sommer_winter_betrieb | 001. Summer-/Winter operation mode (1=Summer, 2=Winter) | 001. Sommer_Winter_Betrieb (1=Sommer, 2=Winter) | 1 | 1 | 2 | 1 | 0
Luftstufe | 002. Ventilation level (0=Stdby, 1=Level1, 2=Level2, 3=Level3, 4=Basic) | 002. Luftstufe (0=Stdby, 1=LS1, 2=LS2, 3=LS3, 4=Grundlüftung) | 2 | 0 | 4 | 1 | 0
EWT_sommer | 003. Geothermal heat exchanger switching point summer | 003. EWT_Sommer | 3 | 0 | 2000 | 0.1 | -1000
EWT_winter | 004. Geothermal heat exchanger switching point winter | 004. EWT_Winter | 4 | 0 | 2000 | 0.1 | -1000
Bypass_schaltpunkt | 005. Bypass switching point | 005. Bypass_Schaltpunkt | 5 | 0 | 2000 | 0.1 | -1000
Konfiguration | 006. Configuration (1=Geothermal heat exchanger, 2=Preheater, 3=Extract defrosting, 4=Preheater 0-100%) | 006. Konfiguration (1=EWT, 2=VorHeiz, 3=Abluft Abtau, 4=SSR) | 6 | 1 | 4 | 1 | 0
Regelung | 007. Temperature control (1=Extract air, 2=Supply air, 3=Room air) | 007. Regelung NHR (1=Abluft, 2=Zuluft, 3=Raum) | 7 | 1 | 3 | 1 | 0
Nachheizregister | 008. Post-heater (0=None, 1=Water, 2=Electrical) | 008. Nachheizregister (0=Kein, 1=Wasser, 2=Elektrisch) | 8 | 0 | 2 | 1 | 0
Luftstufe1 | 009. Ventilation level 1 | 009. Luftstufe1 | 9 | 3 | 40 | 10 | 0
Luftstufe2 | 010. Ventilation level 2 | 010. Luftstufe2 | 10 | 4 | 40 | 10 | 0
Luftstufe3 | 011. Ventilation level 3 | 011. Luftstufe3 | 11 | 3 | 40 | 10 | 0
Grundluftung | 012. Basic ventilation | 012. Grundlüftung | 12 | 3 | 40 | 10 | 0
Luftdifferenz | 013. Air volume flow difference, ETA-Balance | 013. Luftdifferenz | 13 | 0 | 100 | 1 | -50
Abtau_ein | 014. Defrost_On | 014. Abtau_Ein | 14 | 0 | 2000 | 0.1 | -1000
Abluft_Abtau_zeit | 015. Defrost time | 015. Abtau_Zeit | 15 | 0 | 1000 | 1 | 0
Abtau_pause | 016. Defrost pause | 016. Abtau_Pause | 16 | 0 | 1000 | 1 | 0
Abtau_differenz | 017. Defrost difference | 017. Abtau_Differenz | 17 | 0 | 1000 | 0.1 | 0
Zuluftstop_timer | 018. Supply fan stopping time | 018. Zuluftstop_Timer | 18 | 0 | 1000 | 1 | 0
Drehzahl_grenze | 019. Defrost_Speed limit exhaust fan | 019. Drehzahl_Grenze | 19 | 0 | 10000 | 1 | 0
Zuluft_max_temperatur | 020. Maximum supply air temperature | 020. Zuluft_max_Temperatur | 20 | 0 | 2000 | 0.1 | -1000
Zuluft_min_temperatur | 021. Minimum supply air temperature | 021. Zuluft_min_Temperatur | 21 | 0 | 2000 | 0.1 | -1000
ZuluftSollwert | 022. Supply air temperature setpoint | 022. Zuluftsollwert | 22 | 0 | 2000 | 0.1 | -1000
RaumSollwert | 023. Room air temperature setpoint | 023. Raumsollwert | 23 | 0 | 2000 | 0.1 | -1000
AbluftSollwert | 024. Extract air temperature setpoint | 024. Abluftsollwert | 24 | 0 | 2000 | 0.1 | -1000
KP_Heizen | 025. KP_Heating | 025. KP_Heizen | 25 | 0 | 10000 | 1 | 0
TI_Heizen | 026. TI_Heating | 026. TI_Heizen | 26 | 0 | 10000 | 1 | 0
Mischertakt | 027. Mixing valve cycle time | 027. Mischertakt | 27 | 0 | 1000 | 1 | 0
Mischerzeit | 028. Mixing valve running time | 028. Mischerzeit | 28 | 0 | 6000 | 0.1 | 0
Filter_ladewert | 029. Filter time | 029. Filter_Ladewert | 29 | 0 | 10000 | 1 | 0
EXT_E2_Frost_Stufe3 | 030. External digital input E2 (1=Frost protection, 2=LVL3) | 030. EXT_E2_Frost_Stufe3 | 30 | 1 | 2 | 1 | 0
EXT_Luftstufe3_nachlauf | 031. External digital input E2 - Ventilation level 3 stopping time | 031. EXT_Luftstufe3_Nachlauf | 31 | 0 | 1000 | 1 | 0
Kondensatwanne | 032. Condensate threshold | 032. Kondensatwanne Schwelle | 32 | 0 | 4095 | 1 | 0
Filter_reset | 033. Filtertime Reset (1=Reset, 2=remind later) | 033. Filter Reset (1=Reset 2=später errinern) | 33 | 0 | 2 | 1 | 0
Grundluftung_ein | 034. Configuration ventilation level (0=standby, 1=basic ventilation) | 034. Grundlüftung_Ein | 34 | 0 | 1 | 1 | 0
Powersave_at_stdby | 035. Powersave at Standby | 035. Powersave at StdBy | 35 | 0 | 1 | 1 | 0
Zuluft_Sollwert_takt | 036. Supply air setpoint cycle | 036. Zuluft Sollwert takt | 36 | 0 | 1000 | 1 | 0
Internes_NHR | 037. Internal post heater | 037. Internes NHR | 37 | 0 | 1 | 1 | 0
Internes_NHR_Frischluft_temp | 038. Fresh air temperature (internal post heater) | 038. Frischluft Temperatur (Internes NHR) | 38 | 0 | 2000 | 0.1 | -1000
CO2_Reg_on | 039. CO2 control (0=Off, 1=On) | 039. CO2 reg Aus/An | 39 | 0 | 1 | 1 | 0
CO2_Reg_sollwert | 040. CO2 setpoint | 040. CO2 reg Sollwert | 40 | 0 | 2000 | 1 | 0
CO2_Reg_KP | 041. CO2 KP | 041. CO2 reg KP | 41 | 0 | 10000 | 1 | 0
CO2_Reg_TI | 042. CO2 TI | 042. CO2 reg TI | 42 | 0 | 10000 | 1 | 0
CO2_Reg_Takt | 043. CO2 cycle | 043. CO2 reg takt | 43 | 0 | 10000 | 1 | 0
Hum_Reg_on | 044. Rellative humidity control (0=Off, 1=On) | 044. Luftfeuchtigkeit reg Aus/An | 44 | 0 | 1 | 1 | 0
Hum_Reg_sollwert | 045. Relative humidity setpoint | 045. Luftfeuchtigkeit Sollwert | 45 | 0 | 100 | 1 | 0
Hum_Reg_max_zeit | 046. Relative humidity maximum time in level 3 | 046. Luftfeuchtigkeit stufe 3 max Zeit | 46 | 0 | 10000 | 1 | 0
Sensor_konfig | 047. Sensor configuration (0=1xCo2 & 1xRH, 1=2xCo2, 2=2xRH, 3=No Sensor) | 047. Sensor Konfiguration | 47 | 0 | 2 | 1 | 0
Uhr_Sommer_Winter_auto | 048. Summer/Winter Time change (0=Off 1=Automatic) | 048. Auto Sommer/Winter Uhr zeit Aus/An | 48 | 0 | 1 | 1 | 0
Test_var1 | 050. Test Bypass damper (0=Normal, 1=Heat recovery, 2=Bypass, 3=Preheat, 4=Error) | 050. Test Bypass Klappe funktion. 0=Normal mode, 1=WRG, 2=Bypass, 3=Vorheiz, 4=Error_pos | 49 | 0 | 65530 | 1 | 0
Test_var2 | 051. Test supply air fan (0=OFF, 100=100%) | 051. Test Zuluft ventilator (0=OFF, 100=100%) | 50 | 0 | 65530 | 1 | 0
Test_var3 | 052. Test exhaust air fan (0=OFF, 100=100%) | 052. Test Abluft ventilator (0=OFF, 100=100%) | 51 | 0 | 65530 | 1 | 0
Test_var4 | 053. Test mode (0=OFF, 1=ON+Preheater_OFF, 2=Preheater+VHR_ON, LG250A: 7=K1_On+Preheater_100%, 8=K1_On+Preheater_0%) | 053. Test Modus. (0=OFF, 1=ON+VHR_OFF, 2=ON+VHR_ON) | 52 | 0 | 65530 | 1 | 0
Reset_to_default | 054. Reset to factory settings (Reset with 12345) | 054. Reset to default (To reset enter 12345) | 53 | 0 | 65530 | 1 | 0
Reset_hour_counter | 055. Reset operating hours counter (Enter: 12345) | 055. Reset hour counter (To reset enter 12345) | 54 | 0 | 65530 | 1 | 0
Test_sd_card | 056. Test SD-Card (1=Begin test, Result==2-SD-card=OK, Result==3-SD-Card=NOT OK) | 056. Test SD-Card (Enter 1 to begin test. If result = 2 then is SD-card OK. If result = 3 then is SD-Card NOT ok) | 55 | 0 | 1 | 1 | 0
ZuluftSollwert_abgesenkt | 057. Low supply air temperature setpoint | 057. Zuluftsollwert abgesenkt | 56 | 0 | 2000 | 0.1 | -1000
RaumSollwert_abgesenkt | 058. Low room air temperature setpoint | 058. Raumsollwert abgesenkt | 57 | 0 | 2000 | 0.1 | -1000
AbluftSollwert_abgesenkt | 059. Low extract air temperature setpoint | 059. Abluftsollwert abgesenkt | 58 | 0 | 2000 | 0.1 | -1000
Ventilator_model | 060. Fan type (0=120mm, 1=140mm, 2=160mm) | 060. Ventilator model (0=120mm, 1=140mm, 2=160mm) | 59 | 0 | 2 | 1 | 0
Max_fanspeed_LS1 | 061. Maximum fanspeed difference ventilation level 1 | 061. Max fanspeed LS1 | 60 | 0 | 5000 | 1 | 0
Max_fanspeed_LS2 | 062. Maximum fanspeed difference ventilation level 2 | 062. Max fanspeed LS2 | 61 | 0 | 5000 | 1 | 0
Max_fanspeed_LS3 | 063. Maximum fanspeed difference ventilation level 3 | 063. Max fanspeed LS3 | 62 | 0 | 5000 | 1 | 0
Reset_Eventlog | 064. Reset (1=Clear error log, 2=Reset Filter Error) | 064. Reset Eventlog = 1, Reset Filter Error = 2 | 63 | 0 | 2 | 1 | 0
AHU_type | 065. AHU Type (0=LG150, 1=LG250, 3=LG320) | 065. AHU type (0=LG150, 1=LG250, 2=LG320) | 64 | 0 | 2 | 1 | 0
VHR_SSR_temp | 066. Preheater control temperature (only LG250A) | 066. VHR SSR reg Temperatur | 65 | 0 | 2000 | 0.1 | -1000
VHR_SSR_pid_p | 067. Pre heater SSR Reg KP | 067. VHR SSR reg KP | 66 | 0 | 10000 | 1 | 0
VHR_SSR_pid_i | 068. Pre heater SSR Reg TI | 068. VHR SSR reg TI | 67 | 0 | 10000 | 1 | 0
VHR_SSR_pid_reg_takt | 069. Pre heater SSR PWM Time | 069. VHR SSR PWM zeit | 68 | 10 | 240 | 1 | 0
bypass_model | 070. Bypass damper type (0=2xdamper for LG150, 1=Relay K6 for LG250A) | 070. Bypass model (0= 2xKlappe, 1=Relai K6) | 69 | 0 | 1 | 1 | 0
LS3_timer | 071. Maximum time of ventilation level 3 from control panel (0=OFF) | 071. LS3 timer (0=OFF) | 70 | 0 | 65000 | 1 | 0
Bypass_counter_bypass | 072. Counter bypass position | 072. Klappe Counter Bypass | 71 | 0 | 65000 | 1 | 0
Bypass_counter_WRG | 073. Counter heat recovery position | 073. Klappe Counter WRG | 72 | 0 | 65000 | 1 | 0
Bypass_counter_VHR | 074. Damper counter preheater | 074. Klappe Counter VHR | 73 | 0 | 65000 | 1 | 0
Bypass_M1_time | 075. Damper M1 time (ms) | 075. Klappe M1 time (msek) | 74 | 0 | 65000 | 1 | 0
Bypass_M2_time | 076. Damper M2 time (ms) | 076. Klappe M2 time (msek) | 75 | 0 | 65000 | 1 | 0
ModbusAdresse | 080. Modbus address (1-247) | 080. ModbusAdresse | 79 | 1 | 247 | 1 | 0
ModbusBaudrate | 081. Modbus baud rate (0=9600 , 1 = 19200) | 081. ModbusBaudrate | 80 | 0 | 1 | 1 | 0
ModbusParitet | 082. Modbus parity (0 = NONE, 1 = EVEN, 2 = ODD) | 082. ModbusParitet | 81 | 0 | 2 | 1 | 0
ModbusSchreibenErlaubt | 083. Modbus write (0=Disabled, 1=Enabled) | 083. ModbusSchreibenErlaubt | 82 | 0 | 1 | 1 | 0
Bypass_curent_lim | 100. Bypass current limit | 100. Bypass_curent_lim | 99 | 0 | 1000 | 1 | 0
ZeitProgrammLuftEnable | 104. Time program air volume flow (0=Disable, 1=Enable) | 104. Zeitprogramm Lüftungsstufen (0=Inaktiv, 1=Aktiv) | 103 | 0 | 1 | 1 | 0
ZeitProgrammRaumEnable | 105. Time programm temperature control (0=Disable, 1=Enable) | 105. Zeitprogramm Temperatur (0=Inaktiv, 1=Aktiv) | 104 | 0 | 1 | 1 | 0
FirmwareVerBT | 106. Firmware Version Touch Display | 106. Firmware Version Touch Display | 105 | 0 | 65535 | 1 | 0
AdcNtcsBT | 107. AdcNtcsBT | 107. AdcNtcsBT | 106 | 0 | 65535 | 1 | 0
AdcNtcPCBNtcIntBT | 108. AdcNtcPCBNtcIntBT | 108. AdcNtcPCBNtcIntBT | 107 | 0 | 65535 | 1 | 0
AdcNtcPCBNtcExtBT | 109. AdcNtcPCBNtcExtBT | 109. AdcNtcPCBNtcExtBT | 108 | 0 | 65535 | 1 | 0
CurrentModeBt | 110. CurrentModeBt | 110. CurrentModeBt | 109 | 0 | 65535 | 1 | 0
T2addAtLowPower | 111. T2addAtLowPower | 111. T2addAtLowPower | 110 | 1000 | 1300 | 0.1 | -1000
T2addAtHiPower | 112. T2addAtHiPower | 112. T2addAtHiPower | 111 | 1000 | 1300 | 0.1 | -1000
T2offset | 113. T2-Offset | 113. T2-Offset | 112 | 900 | 1100 | 0.1 | -1000
T2intExtComp | 114. T2 internal to external compensation | 114. T2 intern zu extern Compensation | 113 | 0 | 100 | 0.1 | 0
Language | 115. Language (0=DE, 1=EN, 2=FR, 3=NL, 4=CZ, 5=SVK, 6=IT, 7=SLO, 8=ESP, 9=PL) | 115. Sprache (0=DE, 1=EN, 2=FR, 3=NL, 4=CZ, 5=SVK, 6=IT, 7=SLO, 8=ESP, 9=PL) | 114 | 0 | 7 | 1 | 0
ScreensaverTime | 116. Screensaver time | 116. ScreensaverTime | 115 | 1 | 600 | 1 | 0
LockMainscreen | 117. Lock main screen | 117. LockMainscreen | 116 | 0 | 1 | 1 | 0
ToHomeScreenTimeout | 118. Back to home screen timeout | 118. ToHomeScreenTimeout | 117 | 10 | 600 | 1 | 0
Password | 119. Password | 119. Password | 118 | 0 | 9999 | 1 | 0
UserPassword | 120. User password | 120. UserPassword | 119 | 0 | 9999 | 1 | 0

## Datapoints
Modbus Datapoints ES1015 |  | Funktionscode Lesen: 04 | Input register (3x) Read
Funktionscode Schreiben: -
Name | Description | Beschreibung | Modbus Adress | Number of Decimal | Offset | Ab Firmware Version
PIC_AD_T2 | PIC_AD_T2 | PIC_AD_T2 | 0 | 0 | 0
PIC_AD_T1 | PIC_AD_T1 | PIC_AD_T1 | 1 | 0 | 0
PIC_AD_0_10Vin_S1 | PIC_AD_0_10Vin_S1 | PIC_AD_0_10Vin_S1 | 2 | 0 | 0
PIC_AD_0_10Vin_S2 | PIC_AD_0_10Vin_S2 | PIC_AD_0_10Vin_S2 | 3 | 0 | 0
PIC_AD_24V | PIC_AD_24V | PIC_AD_24V | 4 | 0 | 0
PIC_AD_3V3 | PIC_AD_3V3 | PIC_AD_3V3 | 5 | 0 | 0
PIC_AD_T3 | PIC_AD_T3 | PIC_AD_T3 | 6 | 0 | 0
PIC_AD_T4 | PIC_AD_T4 | PIC_AD_T4 | 7 | 0 | 0
PIC_AD_T5 | PIC_AD_T5 | PIC_AD_T5 | 8 | 0 | 0
PIC_AD_M1and2 | PIC_AD_M1and2 | PIC_AD_M1and2 | 9 | 0 | 0
PIC_AD_Kondens | PIC_AD_Kondens | PIC_AD_Kondens | 10 | 0 | 0
PIC_AD_Pressure_2 | PIC_AD_Pressure_2 | PIC_AD_Pressure_2 | 11 | 0 | 0
PIC_AD_Pressure_1 | PIC_AD_Pressure_1 | PIC_AD_Pressure_1 | 12 | 0 | 0
PIC_AD_Pressure_ref | PIC_AD_Pressure_ref | PIC_AD_Pressure_ref | 13 | 0 | 0
PIC_DIGin_E1 | PIC_DIGin_E1 | PIC_DIGin_E1 | 14 | 0 | 0
PIC_DIGin_E2 | PIC_DIGin_E2 | PIC_DIGin_E2 | 15 | 0 | 0
PIC_Relay_K1 | Relay K1 Preheater, GHX, ODA damper | Relais K1 VHR, EWT, AUL-Klappe | 16 | 0 | 0
PIC_Relay_K2 | Relay K2 Fans | Relais K2 Ventilatoren | 17 | 0 | 0
PIC_Relay_K3 | Relay K3 Water post-heater pump | Relais K3 Wasser-NHR-Pumpe | 18 | 0 | 0
PIC_Relay_K4 | Relay K4 Mixing valve opening/Post-heater level 1 | Relais K4 Mischer öffnen/ENHR Stufe 1 | 19 | 0 | 0
PIC_Relay_K5 | Relay K4 Mixing valve closing/Post-heater level 2 | Relais K4 Mischer schließen/ENHR Stufe 2 | 20 | 0 | 0
PIC_Relay_K6 | Relay K6 Error indication (LG150)/Bypass damper (LG250A) | Relais K6 Fehlermeldung (LG150)/Bypassklappe (LG250A) | 21 | 0 | 0
PIC_SD_Card_present | SD card present | SD-Karte vorhanden | 22 | 0 | 0
PIC_LG150_sw_ver | FW Version controller | FW Version Steuerung | 23 | 1 | 0
PIC_Mini_Panel_sw_ver | FW version operating panel | FW Version Bedieneinheit | 24 | 1 | 0
PIC_LG_Model | LG model | LG Modell | 25 | 0 | 0
PIC_Ventilator_model | Fan type | Ventilatortype | 26 | 0 | 0
TempNtcT6_Raum | T6 Touch Display | T6 Touch Display | 29 | 1 | -1000
TempNtcT1_Frischluft | T1 Outdoor air | T1 Außenluft | 30 | 1 | -1000
TempNtcT2_Fortluft | T2 Exhaust air | T2 Fortluft | 31 | 1 | -1000
TempNtcT3_Abluft | T3 Extract air | T3 Abluft | 32 | 1 | -1000
TempNtcT4_Zuluft | T4 Supply air | T4 Zuluft | 33 | 1 | -1000
TempNtcT5_Aussen_NHR_luft | T5 Outdoor air external (LG250A), Supply air external | T5 Außenluft extern (LG250A), Zuluft extern | 34 | 1 | -1000
S1_0_10Vin | S1 0-10Vin | S1 0-10Vin | 35 | 1 | 0
S2_0_10Vin | S2 0-10Vin | S2 0-10Vin | 36 | 1 | 0
E1_Dig_in | E1 Din ext. Off | E1 Din Ext. Aus | 37 | 0 | 0
E2_Dig_in | E2 Din ext. Level3 | E2 Din Ext. Stufe3 | 38 | 0 | 0
Tacho_U1_Zuluft | Supply fan speed [rpm] | Zuluftventilator Drehzahl [U/min] | 39 | 0 | 0
Tacho_U2_Abluft | Exhaust fan speed [rpm} | Fortluftventilator Drehzahl [U/min] | 40 | 0 | 0
E3_in | Condensate watchdog | Kondensatwächter | 41 | 0 | 0
Pressure_P1 | Pressure_P1 | Pressure_P1 | 42 | 0 | 0
Pressure_P2 | Pressure_P2 | Pressure_P2 | 43 | 0 | 0
Zuluft_steuersignal | SUP fan control signal [V] | ZUL Steuersignal [V] | 44 | 0 | 0
Abluft_steuersignal | EHA fan control signal [V] | FOL Steuersignal [V] | 45 | 0 | 0
Zuluft_volumenstrom | SUP airflow [m³/h] | ZUL-Volumenstrom [m³/h] | 46 | 0 | 0
Abluft_volumenstrom | ETA airflow [m³/h] | ABL-Volumenstrom [m³/h] | 47 | 0 | 0
Betriebsstatus | Operating status | Betriebsstatus | 48 | 0 | 0
Abtau_zeit | Defrost time | Abtauzeit | 49 | 0 | 0
Filtertimer_zeit | Next filter change [h] | Nächster Filterwechsel [h] | 50 | 0 | 0
Bypass_klappe_position | Damper position | Klappenposition | 51 | 0 | 0
Frost_abluft_abtau_status | Frost ExtractAir defrost status | Frost Abluft Abtau Status | 52 | 0 | 0
Frost_abluft_abtau_fehler_counter | Frost ExtractAir defrost error counter | Frost Abluft Abtau Fehlerzähler | 53 | 0 | 0
Mischer_pos | Mixing valve position | Mischerposition | 54 | 0 | 0
Zuluft_sollwert_berechnet | SUP-T setpoint calculated | ZUL-T-Sollwert berechnet | 55 | 1 | 0
CO2_reg_out | CO2 control signal | CO2 Regelsignal | 56 | 0 | 0
Uhr_Summer_Winter_status | Summer/winter time | Uhrzeit Sommer/Winter | 57 | 0 | 0
VHR_SSR_reg_out | Preheater control signal | VHR Ansteuerung | 58 | 0 | 0
Lufter_stufe_aktuel | Current ventilation level | Aktuelle Lüftungsstufe | 59 | 0 | 0
Status_Fehler_Z01 | Z01 T difference GHX | Z01 T-Differenz EWT | 60 | 0 | 0
Status_Fehler_Z02 | Z02 Operating panel | Z02 Bedieneinheit | 61 | 0 | 0
Status_Fehler_Z03 | Z03 Frost protection Din2 | Z03 Frostschutz Din2 | 62 | 0 | 0
Status_Fehler_Z04 | Z04 Exhaust fan shorted | Z04 Fortluftventilator | 63 | 0 | 0
Status_Fehler_Z05 | Z05 Supply fan shorted | Z05 Zuluftventilator | 64 | 0 | 0
Status_Fehler_Z06 | Z06 T1 Outdoor air shorted | Z06 T1 Außenluft Kurzschluss | 65 | 0 | 0
Status_Fehler_Z07 | Z07 T2 Exhaust air shorted | Z07 T2 Fortluft Kurzschluss | 66 | 0 | 0
Status_Fehler_Z08 | Z08 T3 Extract air shorted | Z08 T3 Abluft Kurzschluss | 67 | 0 | 0
Status_Fehler_Z09 | Z09 T4 Supply air shorted | Z09 T4 Zuluft Kurzschluss | 68 | 0 | 0
Status_Fehler_Z10 | Z10 T5 ODA external shorted | Z10 T5 AUL extern (LG250A) Kurzschluss | 69 | 0 | 0
Status_Fehler_Z11 | Z11 T1 Outdoor air open circuit | Z11 T1 Außenluft Unterbrechung | 70 | 0 | 0
Status_Fehler_Z12 | Z12 T2 Exhaust air open circuit | Z12 T2 Fortluft Unterbrechung | 71 | 0 | 0
Status_Fehler_Z13 | Z13 T3 Extract air open circuit | Z13 T3 Abluft Unterbrechung | 72 | 0 | 0
Status_Fehler_Z14 | Z14 T4 Supply air open circuit | Z14 T4 Zuluft Unterbrechung | 73 | 0 | 0
Status_Fehler_Z15 | Z15 T5 ODA(LG250A)_SUP(Post-heater) external open circuit | Z15 T5 AUL(LG250A)_ZUL(NHR) extern Unterbrechung | 74 | 0 | 0
Status_Fehler_Z16 | Z16 Change filters | Z16 Filter wechseln | 75 | 0 | 0
Status_Fehler_Z17 | Z17 Condensate drip tray | Z17 Kondensatwanne voll | 76 | 0 | 0
Status_Fehler_Z18 | Z18 Dampers | Z18 Klappen | 77 | 0 | 0
Status_Fehler_Z19 | Z19 Fan speed difference - basic ventilation | Z19 Ventilatordifferenz - Grundlüftung | 78 | 0 | 0
Status_Fehler_Z20 | Z20 Fan speed difference too high | Z20 Ventilatordifferenz zu hoch | 79 | 0 | 0
Status_Fehler_Z21 | Z21 Post-heater frost protection | Z21 NHR Frostschutz | 80 | 0 | 0
Lufter2_stunde | Operating hours ventilation level 2 | Betriebsstunden Lüftungsstufe 2 | 81 | 0 | 0
Lufter3_stunde | Operating hours ventilation level 3 | Betriebsstunden Lüftungsstufe 3 | 82 | 0 | 0
LufterGrund_stunde | Operating hours basic ventiliation level | Betriebsstunden Grundlüftung | 83 | 0 | 0
Lufter_total_stunde | Total operating hours | Gesamtbetriebsstunden | 84 | 0 | 0
Heat_element_stunde | Operating hours preheater | Betriebsstunden Vorheizregister | 85 | 0 | 0
Bypass_klappe_stunde | Operating hours bypass | Betriebsstunden Bypass | 86 | 0 | 0
Lufter1_stunde | Operating hours ventilation level 1 | Betriebsstunden Lüftungsstufe 1 | 88 | 0 | 0
CO2_S1 | CO2 S1 | CO2_S1 | 89 | 0 | 0
CO2_S2 | CO2 S2 | CO2_S2 | 90 | 0 | 0
Hum_S1 | rF S1 | rF S1 | 91 | 0 | 0
Hum_S2 | rF S2 | rF S2 | 92 | 0 | 0